## Calculator
CUBO2 PLUS Refrigerant Charge Calculator V 1.1 |  |  |  | Save it on your PC before starting to use
UNIT MODEL |  | UMT 150 MTDX
Liquid Receiver model |  | 15 L | 37 Lt model is available just as an OPTION | ***Please, check always the online version to be sure you are using the most updated one***
Use & fill out ONLY the yellow cells |  |  |  | Notes for using this calculator:
Pipework |  | Metres | kg
LIQUID LINE |  |  |  | 1. Select or enter only using yellow cells
Liquid Line 3/8" (120 bar K65) |  | 0 | 0 | 2. Using the drop down menu select the unit model
Liquid Line 1/2" (120 bar K65) |  | 0 | 0 | 3. Using the drop down menu select the 15L or 37L receiver CUBO2 Plus condensing unit
Liquid Line5/8" (120 bar K65) |  | 0 | 0 | 4. Enter your system pipe lengths in meters ensuring you select the correct sizes and pressure rating
Liquid Line 7/8" (120 bar K65) |  | 0 | 0
Sub Total Liquid |  |  | 0 | 5. Use the drop down menu to enter the evaporator charge as either kg's or of dm3 / litres - use the evaporators manufacturers information
6. The calculator will give a total charge and acceptable limits
SUCTION LINE
Suction Line 3/8" (120 bar K65) |  | 0 | 0
Suction Line 1/2" (120 bar K65) |  | 0 | 0
Suction Line 5/8" (120 bar K65) |  | 0 | 0
Suction Line 7/8" (120 bar K65) |  | 0 | 0
Sub Total Suction |  |  | 0
STANDING CHARGE
Receiver |  |  | 3
Gas Cooler |  |  | 2.475
Sub Total CUBO |  |  | 5.475
EVAPORATORS
Total evaporators volume | dm3 (Litres) |  | 0
Sub Total Evaps |  |  | 0
Total Charge (minimum charge is 4kg) | kg | 5.475 | ok
Pumpdown from E2V MUST BE ≤ 25kg for 37L and ≤ 10 for 15L | kg | 3 | ok
Pumpdown from CU Liquid Outlet ≤ 25kg for 37L and ≤ 10 for 15L - If not fit ball valves on branch lines | kg | 3 | ok
Oil to Charge (POE) | Cubo2 Plus are precharged with Oil. Additional oil can be added according to how it is coming back from the evaporators |  | Oil approved: POE Reniso Fuchs C85E or Fuchs BSE 85 K

## Revision Log (hidden)
Revisions
v1.1 - First revision of Charge Calculator | 2021-06-25
|  |  | -5 | -10 | -30
|  | Exp Outlet | 523.4 | 388.6 | 151 | kg/m3
|  | Evap Outlet | 76.86 | 66.12 | 35.07 | kg/m3
|  | Average Density | 300.13 | 227.36 | 93.035 | kg/m3
Source: Danfoss Coolselector2

## Reserved (hidden)
|  |  | Unit Model | GC code | GC description | Fans | GC volume (L) | 25% carica residua nel GC (kg)
Liq Receiver Model | UM |  | UMT 036 MTDX | 4408211 | BAT.GC MCQ2 0722A5404065521CO106 | A3G500 AD01-58 (EBM) | 7.6 | 1.9
15 L | dm3 (Litres) |  | UMT 075 MTDX | 4408211 | BAT.GC MCQ2 0722A5404065521CO106 | A3G500 AD01-58 (EBM) | 7.6 | 1.9
37 L | kg's |  | UMT 120 MTDX | 4408211 | BAT.GC MCQ2 0722A5404065521CO106 | A3G500 AD01-58 (EBM) | 7.6 | 1.9
Precharged Oil | ml | 250 | UMT 150 MTDX | 4408213 | BAT.GC MCQ3 0722A5403121521CO109 | A3G500 AD01-58 (EBM) | 9.9 | 2.475
|  |  | UMT 190 MTDX | 4408213 | BAT.GC MCQ3 0722A5403121521CO109 | A3G500 AD01-58 (EBM) | 9.9 | 2.475
Gas cooler 75m approx. (assume 25% liquid) 1300 |  |  | UMT 030 BTDX | 4408216 | BAT.GC UMT BT 722A5402065521CO2(3+3) | A3G500 AD01-58 (EBM) | 4.6 | 1.15
Hold-up Inner Volume PHE (AQUA): | 0,85 dm3 (Assume 25% liquid: 0,21kg) |  | UMT 035 BTDX | 4408216 | BAT.GC UMT BT 722A5402065521CO2(3+3) | A3G500 AD01-58 (EBM) | 4.6 | 1.15
|  |  | UMT 036 BTDX | 4408216 | BAT.GC UMT BT 722A5402065521CO2(3+3) | A3G500 AD01-58 (EBM) | 4.6 | 1.15
|  |  | UMT 120 BTDX | 4408216 | BAT.GC UMT BT 722A5402065521CO2(3+3) | A3G500 AD01-58 (EBM) | 4.6 | 1.15
Volume di refrigerante residuo nella suction: considerato l'8% del volume del piping
Volume max sicurezza ricevitore: 70%
Standing Charge Liquid Receiver = 3Lt (sia per il 15 sia per il 37lt)
Note: Il modello del GC 4408210 NON è piu’ utilizzato
UMT | 4408210 | BAT.GC MCQ2 0722A5402065521CO104 REV.B | A3G500 AD01-58 (EBM)
UMT | 4408211 | BAT.GC MCQ2 0722A5404065521CO106 | A3G500 AD01-58 (EBM)
UMT | 4408213 | BAT.GC MCQ3 0722A5403121521CO109 | A3G500 AD01-58 (EBM)
UMT | 4408216 | BAT.GC UMT BT 722A5402065521CO2(3+3) | A3G500 AD01-58 (EBM)
Oggetto: R: volumi batterie
SCM p/n | Modine P/n | Volume tot [l]
4115400 | B02332 | 3.6
4408210 | D96470 | 4.5
4408211 | D96523 | 7.6
4408213 | B00793 | 9.9
4408216 | D98836 | 4.6
4408165 | D97448 | 46.1
4408166 | D97749 | 62.4
4408167 | D97809 | 85
4408168 | D97273 | 99.2
4408169 | D97274 | 115