## Calculator
CUBO2 Smart/AQUA Refrigerant Charge Calculator V 4.2 |  |  |  | Save it on your PC before starting to use
UNIT MODEL |  | Cubo2 Smart
Liquid Receiver model |  | 12 L |  | ***Please, check always the online version to be sure you are using the most updated one***
Use & fill out ONLY the yellow cells |  |  |  | Notes for using this calculator:
Pipework |  | Metres | kg
LIQUID LINE |  |  |  | 1. Select or enter only using yellow cells
Liquid Line 3/8" (120 bar K65) |  | 0 | 0 | 2. Using the drop down menu select the 12L, 8L, 2 x 2.4L or 2 x 3,3L receiver CUBO2 Smart condensing unit
Liquid Line 1/2" (120 bar K65) |  | 0 | 0 | 3. Enter your system pipe lengths in meters ensuring you select the correct sizes and pressure rating
Liquid Line 1/2" (80 bar K65) |  | 0 | 0 | 4. Use the drop down menu to enter the evaporator charge as either kg's or of dm3 / litres - use the evaporators manufacturers information
Sub Total Liquid |  |  | 0 | 5. The calculator will give a total charge and acceptable limits
SUCTION LINE
Suction Line 3/8" (120 bar K65) |  | 0 | 0
Suction Line 1/2" (80 bar K65) |  | 0 | 0
Suction Line 1/2" (120 bar K65) |  | 0 | 0
Suction Line 5/8" (80 bar K65) |  | 0 | 0
Suction Line 5/8" (120 bar K65) |  | 0 | 0
Sub Total Suction |  |  | 0
STANDING CHARGE
Receiver |  |  | 3.6
Gas Cooler/ PHE |  |  | 1.3
Sub Total CUBO |  |  | 4.9
EVAPORATORS
Evap 1 | dm3 (Litres) | 0 | 0
Evap 2 | dm3 (Litres) | 0 | 0
Evap 3 | dm3 (Litres) | 0 | 0
Sub Total Evaps |  |  | 0
Total Charge (minimum charge is 4kg) | kg | 4.9 | ok
Pumpdown from E2V MUST BE ≤ 9,6kg for 12L and ≤ 7.2kg for 8L and ≤ 3.5 for 2x2,4L and ≤ 4,4 for 2x3,3L | kg | 3.6 | ok
Pumpdown from CU Liquid Outlet ≤ 9,6kg for 12L and ≤ 7.2kg for 8L and ≤ 3,5 for 2x2,4L and ≤ 4,4 for 2x3,3L - If not fit ball valves on branch lines | kg | 3.6 | ok
Additional Oil to Charge (PAG VG100) | ml | 362.5 | Oil approved: RENISO PAG100, DAPHNE PZ100S

## Revision Log (hidden)
Revisions
v2.1 - Corrected cell 39C, I, O text to 3.5kg
V2.2 - Added 1/2" to 8L
V2.3 - Added Revision Log
V2.3 - Added 1/2" Liquid to 2 x 2.4L
V2.4 - SCMFrigo Customization
V2.5 - Locked cells and tidied text
V2.6 - Added 5/8" Suctions
V2.7 - Added Oil charge calculation
V2.8 - Change Oil Charge calculation and some formats
V2.9 - Changed Total Charge ! To Stop! Charge Exceeded
V3.0 - Added the option for Cubo2 AQUA charge calculator
V4.0 - Changed evap refrigerant density, averaged exp outlet and evap outlet -5DegC data used
V4.1 - Added the option for 2x3,3 Lt Liquid Receiver
V42 - Added the option for 12 Lt Liquid Receiver
|  | -5 | -10 | -30
| Exp Outlet | 523.4 | 388.6 | 151 | kg/m3
| Evap Outlet | 76.86 | 66.12 | 35.07 | kg/m3
| Average Density | 300.13 | 227.36 | 93.035 | kg/m3
Source: Danfoss Coolselector2

## Reserved (hidden)
|  |  |  | Liq. Receiver Volume (lt) | Standing Charge (lt) | Max Charge (lt)
Liq Receiver Model | UM |  | Cubo2 Smart
8 L | dm3 (Litres) |  | Cubo2 AQUA | 8 | 2.4 | 7.2
2x2,4 L | kg's |  |  | 4.8 | 1.2 | 3.5
2x3,3 L |  |  |  | 6.6 | 1.6 | 4.4
12 L |  |  |  | 12 | 3.6 | 9.6
Precharged Oil | ml | 250
Gas cooler 75m approx. (assume 25% liquid) 1300
Hold-up Inner Volume PHE (AQUA): | 0,85 dm3 (Assume 25% liquid: 0,21kg)